## Instruction Sheet
INSTRUCTION FOR FILLING UP THE FORM-Sh
Sr No | Details | Basis/Formule | Note | Frequency | Primary Documents from where the information can be sourced and to be kept ready for verification by Accredited Energy Auditor | Secondary Documents from where the information can be sourced and to be kept ready for verification by Accredited Energy Auditor
It is mandatory to fill all the fields of Excel sheets-General Information sheet and Form Sh, For Baseline Year and assessment year, if otherwise specified
Please fill the data as per colour coding provided at the bottom of Form Sh
The DC may submit separate Excel sheet for additional information required for Heat Rate calculation or Normalisation for different module combination or load
1 | Please provide the name of unit /Station | To be filled in the General Information Sheet
1a | Please fill ithe PAT cycle applicable | To be selected from the dropdown in the General Information Sheet cell no. F3
1b | Please fill the year | to be filled in form sh cell nos. E7 and M7
1c | Current/ Assessment/ Target Year (20.... 20....) | to be filled in form sh cell no. E7 | If the form is being submitted for assessmet year, then the assessment year has to be mentioned. If it is being submitted for filing energy return, then the current year shall be written
1d | Baseline Year/ Previous Year (20.... 20....) | to be filled in form sh cell no. M7 | If the form is being submitted for assessmet year, then the baseline year has to be mentioned. If it is being submitted for filing energy return, then the previous financial year shall be written
2 | Please provide the year of establishment of the Station | To be filled in the General Information Sheet
3 | Please provide the type of the Station | To be filled in the General Information Sheet. .
4 | Plant Details
i | Please provide the total MW installed Capacity of the Station | To be filled in the Form-Sh Sheet directly | 1. Form Sh is to be filled for Gas/Oil Fired Thermal Power plant also, however the Normalisation for Fuel Mix will be dealt separately. 2. The other calculation will be performed based on the mearit of the parameters in Form Sb | One time | COD document | PPA
ii | Please provide unit configuration (i.e. 3x100 + 2x250 + 2x500+ ------- etc.) of the Station | To be filled in the Form-Sh Sheet directly |  | One time | COD document | PPA
iii | Notified Baseline Net Heat Rate (kcal/kWh) |  |  | One time | Notification S.O. 387 (E ) | Calculation for target setting
iv | Notified Target Net Heat Rate (kcal/kWh) |  |  | One time | Notification | Calculation for target setting
v | Notified Net Product output (Net Generation) in Million Units |  |  | One time | Notification | Calculation for target setting
vi | % Reduction Target for Percentage deviation in the Station Net Heat Rate as per Notificataion | Shall be calculated as per the formula given in the PAT documents |  | One time | Notification | Calculation for target setting
5 | Unit wise Design Data Details
5 | Please provide the Unitwise design installed Capacity, Boiler Efficiency, Turbine Heat rate and Unit Heat rate provided by Original Equipment Manaufacturer (OEM) and as per Performance Guarantee Test (PG Test) report and the Commercial Operation Date (COD) of all the Unit. The data to be provided for Major Fuel | Unit Design Heat Rate (UDHR) = Turbine Heat Rate /Boiler Efficiency, & COD in terms of Date format xx/xx/xxxx |  | One time | 1. OEM Curves and docuemts/ COD documents 2 PG Test Report 3. HMB diagram at different load (Minimum 5-7 nos of (x,y) co-ordinates to plot as curve 4. Design Boiler Efficiency Document from Original Equipment Manufacturer (OEM) 5. Design Coal Analysis Document as per OEM 6. Predicted Performance Data (PPD) document from OEM | 1.Plant Design document from OEM 2. PG Test Report
5.1 | Calculation for Station installed Capacity, Boiler Efficiency, Turbine Heat rate and Unit Heat rate provided by Original Equipment Manaufacturer (OEM) and as per Performance Guarantee Test (PG Test) report and the commercial operation date (COD) of all the Unit. | Station's Design Heat Rate = [UDHR1xC1 + UDHR2xC2+ UDHR3xC3………]/[C1+C2+C3…….] Where C1, C2, C3, …..= Unit Capacity in MW |  | One time
5.2 | Please provide the Unitwise design installed Capacity, Boiler Efficiency, Turbine Heat rate and Unit Heat rate provided by Original Equipment Manaufacturer (OEM) and as per Performance Guarantee Test (PG Test) report and the Commercial Operation Date (COD) of all the Unit. The data to be provided for Other Fuel |  |  | One time | 1. OEM Curves and docuemts/ COD documents 2 PG Test Report 3. HMB diagram at different load (Minimum 5-7 nos of (x,y) co-ordinates to plot as curve 4. Design Boiler Efficiency Document from Original Equipment Manufacturer (OEM) 5. Design Coal Analysis Document as per OEM | 1.Plant Design document from OEM 2. PG Test Report
6 | Unit wise Operating Data Details
6.a | Please provide the Unitwise Operating details such as Operating Load, Unit Load factor, Gross Generation, Unit Heat rate for the present year as well as for the previous year | To be filled in the Form-Sh Sheet directly |  | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6) Internal Audit Report 7) Efficiecny Report
6.b | Please provide the Station's Operating details such as Operating Load, Plant Load factor, Gross Generation, Station Heat rate for the present year as well as for the previous year. | Station Operating Gross Heat Rate = [(OGHR 1 x Generation 1 + OGHR 2 x Generation 2 + -----------) / (Total Generation of Station)] |  | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6) Internal Audit Report
7 | Station's Generation & PLF details/ Other Details |  |  | Primary-Annual Secondary-Daily reports | Annual Generation Reports | Daily Generation Reports
| Plant Details | as per Sr No 4 (i)
i | Please provide installed capacity (MW) of the station for current as well as for the previous year | if the COD of a 200 MW unit is 1st October, its weighted capacity for the whole year is |  |  | 1. OEM Document
ii | If COD of some unit(s) is in between the year, Please provide the total station's weighted capacity for the year in MW | For example : if the COD of a 200 MW unit is 1st October in the current year, its weighted capacity for the whole year is 100 MW |  |  | 1. COD Document submitted to Authority
iii | Please provide total Gross Generation (MU) of the station for current as well as for previous year | Total Gross Generation = Gen1 + Gen2 +Gen3+……… |  | Primary-Annual Secondary-Daily reports | 1. Annual Generation Reports 2. DGR 3. MGR 4. Annual Report | 1. Energy Management System 2. Energy Meters
iv | Calculation of Plant Availability Factor (%) | The calculation is to be done from Planned or unplanned staoppages, Forced outage etc of unit |  | Daily, Monthly, Annual | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Generation Schedule from Load Despatch Centre 5) External Breakdown Report 6) Fuel Unavailability document/record from external agencies 7) Coal Linkage Document 8) Log Book | 1) Shift Register 2) Shift Reports 3) Energy Meter Readings 4) Energy Management System 5) Breakdown reports (Internal and External)
v | Please provide total Plant Load factor (%) of the station for current as well as for previous year | Plant Load Factor (%) = Gross generation (MU)/(Installed Capacity (MW) X 8.76) | Example-For Calculating ULF of the unit commissioned during the year : if the COD of a 200 MW unit is 1st October and PLF for the remaining period is 80% , its weighted capacity for the whole year is 100 MW, with weighted for whole year PLF stands at 40% | Primary-Annual Secondary-Daily reports | 1. Annual Generation Reports 2. DGR 3. MGR 4. Annual Report | 1. Energy Management System 2. Energy Meters
vi | Reference from other cell: Auxiliary Power Consumption (APC) in MU | APC = Gross Genration - Generation send out to grid | The Auxilliary Power of the Station to be provided without Colony and construction power | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
vii | Calculation of Auxiliary Power Consumption (APC) in %
viii | Calculation of operating gross heat rate of the station | same as calculated in row no. 6.b |  | Primary -Daily Secondary- Daily | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6. Efficiency Report
ix | Calculation of operating Net heat rate (ONHR) of the station. | ONHR = OGHR/(1-APC/100) |  | Primary -Daily Secondary- Daily | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Coal Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Weigh feeder 4) Bunker load Cells 5) Fuel GCV test report (Internal and External) 6. Efficiency Report
x | Please provide the Average PLF during Baseline year as per baseline energy audit reports |  |  |  | 1) baseline Report
xi | Please provide Actual PLF as reported to CERC/SERC |  |  |  | 1) Reporting document to CERC/SERC
xii | Please provide the Operation Norms for Thermal Power Stations Gross Heat rate Tariff Period - 2014 - 19 as per CERC/SERC |  |  |  | 1)Tariff Document from CERC
xiii | Reference from other Cell: Station Net Operating Heat Rate as per Notification (Baseline)
xiv | Reference from other Cell: Station Net Target Heat Rate as per Notification (Baseline)
7.1 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii) in case of Gas based Power Station or Thermal Oil-Gas based Plant)
a | Please provide the Annual Genertion for Actual Gross Generation-Closed Cycle in differnet type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  | DC to provide the details of generation through Gas or Oil field for Gas or Oil based Thermal Power Plant | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Fuel Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Fuel Flow Meter 4) Gas Meter 5) Fuel GCV test report (Internal and External) 6. Efficiency Report 7. GCV/NCV test report from external or internal test report
b | Please provide the Annual Genertion in MU for Actual Gross Generation-Open Cycle due to Internal factor in differnet type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  | DC to provide the details of generation through Gas or Oil field for Gas or Oil based Thermal Power Plant | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Fuel Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Fuel Flow Meter 4) Gas Meter 5) Fuel GCV test report (Internal and External) 6. Efficiency Report 7. GCV/NCV test report from external or internal test report
c | Please provide the Annual Genertion in MU for Actual Gross Generation-Open Cycle due to External factor in differnet type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  | DC to provide the details of generation through Gas or Oil field for Gas or Oil based Thermal Power Plant | Primary-Annual Secondary-Hourly shift log book/ Daily reports | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Unit Log book 5) Fuel Consumption records 6) Stores Stock Register 7)Purchase Order 8) SAP Entry in PP/SD mosule | 1) Generator Energy Meter (Sealed) 2) Energy Management System 3) Fuel Flow Meter 4) Gas Meter 5) Fuel GCV test report (Internal and External) 6. Efficiency Report 7. GCV/NCV test report from external or internal test report
7.2 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii), 7(vi) in case of Gas based Power Station)
i | Please provide the Auxiliary Power Consumption in MU for different type of plant operation through Gas/Naptha/Oil/Other Fuel in Gas based CCGT or Gas based Thermal Power Station |  |  | Primary-Annual Secondary-Hourly shift log book/ Daily reports | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
ii | Reference from other Cell:Actual Gross Generation-Closed Cycle
iii | Reference from other Cell:Actual Gross Generation -Open Cycle due to internal factor
iv | Reference from other Cell:Actual Gross Generation-Open Cycle due to external factor
v | Reference from other Cell:Actual Gross Generation
vi | calculation: Auxiliary Power Consumption
8 | Details of Electricity Purchased from the Grid (MUs)
i | Please provide the purchased electricity if any. |  |  |  | 1) Grid Meter report 2) Daily Power Report 3) DGR 4) MGR | 1) Meter Reading 2) Energy management System
ii | Please provide the reason if plant has purchased electricity |  |  |  | Basis Report
9 | Details of Electricity Generated
i | Reference from other Cell:Total Gross Generation of Electricity | To be filled in the Form-Sh Sheet directly |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
ii | Reference from other Cell:Total Net Electricity Supplied to Grid | Total Supplied to grid =Total Generation -APC |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
iii | Please provide Electricity Consumption-Colony/Construction | To be filled in the Form-Sh Sheet directly |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
iv | Total Electricity used inhouse for Power Generation i.e. APC (Without colony, construction & others consumption) |  |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
v | Any other (specify) | To be filled in the Form-Sh Sheet directly |  | Primary -Daily Secondary- Hourly | Daily Generation Reports | Energy Meter Readings for Bus/ boards/ transformers & Export/ Import/ Switchyard report
10 | Unitwise Fuel Analysis Details (As Fired Basis)
10. 1. | Please provide the Unitwise Solid Fuel's (Coal/Lignite Fuel) Proximate and Ultimate Analysis details in row 10.1 A to 10.1.J for design fuel, PG test fuel, current year and as well for previous year fuel used for Electricity Production/Generation. |  |  | Primary-daily secondary- every 4 hours | 1) Daily Internal Report from Lab on Fuel Proximate Analysis performed on each lot. 2) Test Certificate from Government Accredited lab. (Plant to maintain minimum 1 sample test in a quarter for Proximate and Ultimate Analysis i.e. 4 test certificates in a year for each soild fuel 3) Purchase Order, where guaranteed GCV range is mentioned | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document
10.1 | Values of ultimate analysis | To be calculated as per section 10.1.1. and filled in the Form-Sh Sheet directly
a | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant | Energy Consumption to be entered in Form Sh |  | Primary-daily secondary- every 4 hours | DGR | Energy Meter Reports
10. 2. | Please provide the Gas fuel Analysis for design fuel, PG test fuel, Current year and as well for Previous year fuel used for Electricity Production/Generation. | Conversion factor from GCV to NCV in the baseline year shall be 1.1 or as submitted by the Gas suppler |  | Primary-daily secondary- every 4 hours | 1) Test report from Supplier 2) Lab analysis report for samples at various points | FSA, Lab analysis report for samples at various points
11 | Details of Fuel Consumption as fired basis
11.1 | Please provide the Gross Calorific Value, Total Consumption and Specific Fuel Consumption of Solid Fuels (Coal/Lignite/others) as fired basis | Specific Fuel Consumption = Quantity of Fuel Energy input to Plant X Gross GCV of Fuel/ output generated from palnt | Landed cost of Fuel is required to calculate the price of 1 ESCerts for the year 2014-15. | Primary-daily/ shift wise secondary- every 4 hours | 1) Daily Internal Report from Lab on Fuel Proximate Analysis performed on each lot. 2) Test Certificate from Government Accredited lab. (Plant to maintain minimum 1 sample test in a quarter for Proximate and Ultimate Analysis i.e. 4 test certificates in a year for each soild fuel 3) Purchase Order, where guaranteed GCV range is mentioned 4) DGR 5) MGR 6) Log Book | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document 6) FSA 7) Lab reports, 8) weighbridge reports 9) stacking reports
11.2 | Please provide the Gross Calorific Value (GCV), Total Consumption and Specific Fuel Consumption of Liquid Fuels (FO/LSHS/HSHS/Diesel/LDO/Any Other) as fired basis | Specific Fuel Consumption = Quantity of Fuel Energy input to Plant X Gross GCV of Fuel/ output generated from palnt |  | Primary-daily/ shift wise secondary- every 4 hours | 1) Purchase Order 2) Stores Receipt 3) SAP Entry in MM/PP/FI module 4) Annual Report 5) DGR 5) MGR | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document 6) FSA 7) Lab reports, 8) weighbridge reports 9) Flow Meter 10) Dip measurement in day tank
11.3 | Please provide the Gross Calorific Value, Total Consumption and Specific Fuel Consumption of Gaseous Fuels (NG/RLNG/APM/Others) as fired basis | Specific Fuel Consumption = Quantity of Fuel Energy input to Plant X Gross GCV of Fuel/ output generated from palnt |  | Primary-daily/ shift wise secondary- every 4 hours | 1) Purchase Order 2) Stores Receipt 3) SAP Entry in MM/PP/FI module 4) Annual Report 5) DGR 5) MGR | 1) internal test report 2) Callibration report of measuring equipment 3) Lab register 4) Lab analysis prcedure documents 5) Sampling methodology document 6) FSA 7) Lab reports, 8) weighbridge reports 9) Flow Meter 10) Dip measurement in day tank
12 | Normalisation Factors to be considered during assessment year
12.1 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors
i | Please provide unitwise loss of generation in MU caused by low ULF due to Coal Unavailability,due to Scheduling, due to backing down, or due to any other external factor for current year as well as for previous year |  |  | Continuous, Daily, Monthly | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Generation Schedule from Load Despatch Centre on daily-blockwise basis 5) External Breakdown Report 6) Fuel Unavailability document/record from external agencies 7) Coal Linkage Document 8) Stores Stocks Register 9) SAP Entry in PP/SD/PM Module 10) Stocks duration report 11) Log Book | 1) Purchase order 2) Rail Racks details 3) Weighing Document 4) Shift Register 5) Shift Reports 6) Energy Meter Readings 7) Energy Management System
12.2 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors/Internal Factor
i | Please provide unit wise operation hours (Hours) caused by Forced Outage/ Unavailability, Planned Maintenance Outage/ Planned Unavailability and Average Operating Load (MW) and with Operating hours due to Internal factor for baseline year and Assessment year | Weighetd Operating Load = [Average Operating Load (MW) due to coal unavailability X operating Hour + Average Operating Load (MW) due to scheduling X Operating hours + Average Operating Load due to backing down X Operating Hour] / [ total average operating load (MW) X Total operating Hour] |  | Primary-Daily Secondary- hourly | 1) Daily Generation Report 2) Monthly Generation Report 3) Shift Report and Register 4) Generation Schedule from Load Despatch Centre 5) External Breakdown Report 6) Fuel Unavailability document/record from external agencies 7) Coal Linkage Document 8) Log Book | 1) Shift Register 2) Shift Reports 3) Energy Meter Readings 4) Energy Management System 5) Breakdown reports (Internal and External)
ii | Please provide the following Documents listed below:
i. Characteristics Curve of Unit Turbine Heat Rate Vs Load, from Original Equipment Manaufacturer (OEM)
ii. Unit wise HBD or Curve from Original Equipment Manufacturer (OEM) at various loads
iii. In case of non-availability of HBD or Curve, data from the similar Unit will be considered
iv. Design/PG Test Turbine Heat Rate documents
12.3 | APC
a | Please enter the APC as per the baseline audit report |  |  | One Time | Annual Report | Audit Report
12.4 | Startup and Stoppages due external factor/Unforeseen factors
A.i | Please provide total number of shutdown in a year separately operating through different fuel Gas/Coal due to Internal and external factor in Nos |  |  | Primary- Annual Secondary-As & when occurred | Annual Reports | Trip reports/ Shift Reports/ Synchronization communication
A.ii | Please provide total number of shutdown in a year due to external factor eparately operating through different fuel Gas/Coal due to external factor in Nos |  |  | Primary- Annual Secondary-As & when occurred | Annual Reports | Trip reports/ Shift Reports/ Synchronization communication
B.i | Please provide the Electrical Energy Consumption during shutdown due to external factor in MU |  |  | Primary- Annual Secondary-As & when occurred | 1) DGR 2) MGR 3) Annul Report 4) SAP Entry in PP/SD/PM Module | 1) Energy Meters 2) Daily Power Report 3) Energy Management System 4) Trip reports/ Shift Reports/ Synchronization communication
C | Please provide total number of Cold/Warm/Hot startup in a year due to external factor in Nos | DC to follow the defination of Cold/Worm/Hot start as defined in the OEM document of Turbine on temperature |  | Primary- Annual Secondary-As & when occurred | 1) OEM document for Turbine 2) DGR 3) MGR 4) Annul Report 5) SAP Entry in PP/SD/PM Module 6) External factor document | Trip reports/ Shift Reports/ Synchronization communication
12.5 | Increase in APC consumption due Environmental Compliance
i | Please provide the name, commitioning date , kw rating , actual operating hour and total energy consumptiion of equipments installed to meet the environmental complience in AY and BY |  | This includes the installation of additional equipment/ system to meet environmental compliance/ concern that came into effect after the baseline year | One time | 1) OEM Documents 2) Purchase order of equipment 3) Shift Log book 4) Shift Register | 1) Energy Meter reading 2) Energy Management System
12.6 | Additional Energy due to Unforeseen circumstances (External Factor) |  |  | Monthly | Monthly Generation/ operation reports | Efficiency Cell Reports
i | Please enter Total Thermal Energy consumption due to unforseen circumstances |  | Unforeseen circumstances could be anything due to external factors that has not been covered in form sh, any energy consumption for construction of new units, etc. | Monthly | 1) Monthly Generation 2) Operation reports 3) Unforeseen Circumstances Documents | Efficiency Cell Reports
ii | Please enter Total Electrical Energy consumption due to unforseen circumstances |  | Unforeseen circumstances could be anything due to external factors that has not been covered in form sh, any energy consumption for construction of new units, etc. | Monthly | 1) Monthly Generation 2) Operation reports 3) Unforeseen Circumstances Documents | Efficiency Cell Reports
13 | Documentation for Normalisation
i | The list of documents that shall be submitted by the DCs is mentioned. The DC shall submit the doc and write Yes/No in the relevant docuembt column | 1) For Normalisation factors, which became applicable due to external factors, authentic documents to be produced by DC for the baseline as well for the assessment year. In absence of these authentic documents, no Normalisation Factor will be applied/Considered. 2) While selecting "No" from the drop down list, the inbuilt calculation automatic treat the Normalisation for particular factor as zero. However, DC needs to submit an undertaking from the Authorised Signatory on non-availability of document
14 | Investment made and Saving Achieved
i | Investment, if any, during this period has to be mentioned with quantified savings in terms of million kcal of coal, lignte, petcoke, biomass/ waste
15 | Process Flow Diagram Attached
i | The process flow diagram has to be attached indicating the entire scheme of the system/ sub-system
ii | The process flow diagram should also clearly indicate the location of auto-sampler and sampling points
Note | For Thermal Power Station firing Gas/ Oil/ Other Fuels in Boiler
Section 5 | All the relevant details with Gas fuel shall be entered | Unit Design Heat Rate (UDHR) = Turbine Heat Rate /Boiler Efficiency, |  | One time | OEM Curves and docuemts/ COD documents | PG Test Reports/ Certified reports on Fuel Change
Section 5.2 | All the relevant details with Oil/Other Fuel shall be entered | Station's Design Heat Rate = [UDHR1xC1 + UDHR2xC2+ UDHR3xC3………]/[C1+C2+C3…….] Where C1, C2, C3, …..= Unit Capacity in MW |  | One time | OEM Curves and docuemts/ COD documents | PG Test Reports/ Certified reports on Fuel Change
16 | Machine Details
i | the name of OEM of Boiler Turbine and PG test to be mentioned
ii | The date of last AOH, COH R&M/LE to be mentioned
17 | Fuel reconciliation document
i | Coal stock reconciliation document for each month to be provided |  |  | Monthly | SAP records/ monthly reports
ii | Coal purchase receipts/ GRN/ and purchase contract document to be attached |  |  | daily/ as applicable | Coal purchase receipts/ GRN | purchase contract document
iii | Gas receipts as received the the supplier |  |  | daily/ as applicable | Gas purchase receipts | purchase contract document
iv | Fuel oil receipts |  |  | daily/ as applicable | Fuel oil purchase receipts | purchase contract document
18 | Note
(i) | The hard copy/Printouts is to be signed by Authorised signatory, if SAP data is used as documents
19 | Abbreviations
MPR | Monthly Production Report
DPR | Daily Production Report
MM | Material Management
PP | Production and Planning
SD | Sales and Distribution
FI | Financial Accounting
PM | Plant Maintenance
AOH | Annual overhauling
COH | Capital overhauling
EMS | Energy Management System

## Form-1
Form-1
Details of information regarding Total Energy Consumed and Specific Energy Consumption Per unit of Production (See Rule 3)
A. | General Details | Description
1 | Name of the Unit | 0
2 | i) Year of Establishment | 0
| (ii) Registration No (As provided by BEE) | 0
3 | Sector and Sub-Sector in which the Designated Consumers falls | Sector |  | Sub-Sector
|  | Sector - Thermal Power Plant |  | Coal/Lignite/Oil/Gas Fired
4. (i) | Complete address of DCs Unit location (including Chief Executive's name & designation) with mobile, telephone, fax nos. & e-mail. | , , , - , Telephone- , Fax- , Plant's Chief Executive Name-, , Telephone with STD Code- , Fax- , Mobile-, E-mail-
(ii) | Registered Office address with telephone, fax nos. & e-mail | Company's Chief Executive Name:,Designation:,Address:,City/Town/Village-,P.O.-, District-,State-,Pin-, Telephone-,Fax-
(iii) | Energy Manager's Name, designation, Registration No., Address, Mobile, Telephone, Fax nos. & e-mail | , , , EA/EM Registration No.- , Telephone-, Fax- , Mobile- , E-mail ID-
B. | Production details
5 | Manufacturing Industries notified as Designated Consumers
| Products | Unit | Previous Year | Current Year
(i) | Product 1 | Tonne
(ii) | Product 2 | Tonne
(iii) | Product 3 | Tonne
(iv) | Product (Please add extra rows in case of additional products) | Tonne
(v) | Total Equivalent Product | Tonne
C | Energy Consumption Details of Manufacturing Industries notified as Designated Consumers
6. (i) | Total Electricity Purchased from Grid/Other Source | Million kwh
(ii) | Total Electricity Generated | Million kwh
(iii) | Total Electricity Exported | Million kwh
(iv) | Total Electrical Energy Consumption | Million kwh
(v) | Total Solid Fuel Consumption | Million kCal
(vi) | Total Liquid Fuel Consumption | Million kCal
(vii) | Total Gaseous Fuel Consumption | Million kCal
(viii) | Total Thermal Energy Consumption | Million kCal
(ix) | Total Normalized Energy Consumption (Thermal+Electrical) | TOE
D | Specific Energy Consumption Details
7. i | Specific Energy Consumption(Without Normalization) | TOE/Tonne
ii | Specific Energy Consumption (Normalized) | TOE/Tonne
E | Power Plants notified as Designated Consumer
8. i. | Total Capacity | MW | 0 | 0
ii | Unit Configuration | No. of units with their capacity | 0 | 0
iii | Annual Gross Generation | MU | 0 | 0
iv | Annual Plant Load Factor (PLF) | % | 0 | 0
v | Station Gross Design Heat Rate | kcal/kWh | 0 | 0
vi | Station Gross Operative Heat Rate | kcal/kWh | 0 | 0
vii | Auxiliary Power Consumption | % | 0 | 0
viii | Operative Net Heat Rate | kcal/kWh | 0 | 0
ix | Operative Net Heat Rate (Normalized) | kcal/kWh |  | 0
F | Sector-Specific Details
S.No | Name of the Sector | Sub-Sector | Form in which the details to be furnished
(i) | Aluminium | Refinery/Smelter | Sa1
|  | Cold Rolling Sheet | Sa2
(ii) | Cement | Cement | Sb
(iii) | Chlor-Alkali | Chlor-Alkali | Sc
(iv) | Fertilizer | Fertilizer | Sd
(v) | Iron and Steel | Integrated Steel | Se1
|  | Sponge Iron | Se2
(vi) | Pulp and Paper | Pulp and Paper | Sf
(vii) | Textile | Composite | Sg1
|  | Fiber | Sg2
|  | Spinning | Sg3
|  | Processing | Sg4
(viii) | Thermal Power Plant | Thermal Power Plant | Sh
I/we undertake that the information supplied in the Form 1 and pro- forma is accurate to the best of my knowledge and the data furnished in Form 1 has been adhered to the data given in the concerned pro forma.
Authorised Signatory and Seal
Signature:-
Name of Energy Manager:
Name of Authorised Signatory |  |  | Registration Number:
Name of the Designated Consumer:
Full Address:-
Seal
Date

## General Information
Form-Sh (General Information)
Sector - Thermal Power Plant
Perform Achieve and Trade (PAT) Cycle |  |  |  | New DC | PAT-III | pl. specify here (if selected 'others')
1 | Name of the Thermal Power Station
2 | i) Year of Establishment |  |  | Basline year/ Previous year | Baseline Year/ Previous Year (2015-2016) | Not a leap year | 8760
| (ii) Registration No (As provided by BEE) |  |  | Current/ Assessment/ Target Year | Current/ Assessment/ Target Year (2019-2020) | Leap year | 8784
3 | Type of Thermal Power Plant | Coal/Lignite/Oil/Gas Fired | Coal/Lignite/Oil/Gas Fired
4 | Plant Contact Details & Address
a | Plant Address
i | City/Town/Village
ii | District
iii | State |  |  | Pin
iv | Telephone |  |  | Fax
b | Plant's Chief Executive Name
i | Designation
ii | Telephone with STD Code |  |  | Fax
iii | Mobile |  | E-mail
5 | Registered Office
i | Company's Chief Executive Name
ii | Designation
iii | Address
iv | City/Town/Village |  |  | P.O.
v | District
vi | State |  |  | Pin
vii | Telephone |  |  | Fax
6 | Energy Manager Details
i | Name
ii | Designation |  |  | Whether EA or EM
iii | EA/EM Registration No.
iv | Telephone |  |  | Fax
v | Mobile |  | E-mail ID

## Summary Sheet
Form Sh-Summary Sheet
Name of the Thermal Power Station |  |  | 0
Type of Thermal Power Station |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Basis/Calculation | Unit | Assessment Year (AY) | Baseline Year (BY) | Remarks
A | Station Configuration
A.1 | Total Capacity | As per Form Sh (4 (i)) | MW | 0 | 0
A.2 | Unit Configuration | As per Form Sh (4 (ii)) |  | 0 | 0
A.3 | Year of Establishment | As per Form Sh (2) | Year | 0 | 0
A.4 | Notified Baseline Net Heat Rate (kcal/kWh) | As per Form Sh (4 (iii)) | kcal/kWh |  | 0
A.5 | Notified Target Net Heat Rate (kcal/kWh) | As per Form Sh ( 4 (iv)) | kcal/kWh |  | 0
A.6 | Notified Net Product output (Net Generation) in Million Units | As per Form Sh ( 4 (v)) | MU |  | 0
A.7 | % Reduction Target for Percentage deviation in the Station Net Heat Rate as per Notification | As per Form Sh ( 4 (vi)) | % |  | 0
A.8 | Difference of Notified Baseline Net Heat Rate and Notified Net Heat Rate | (A.4)-(A.5) | kcal/kWh |  | 0
B | Station Design Configuration
B.1 | Station Gross Heat Rate |  | kcal/kwh | 0 | 0
B.2 | Boiler Efficiency |  | % | 0 | 0
C | Station Operating Configuration
C.1 | Gross Generation | As per Form Sh (6. 1) - 'Form Sh'!I49 | MU | 0 | 0
C.2 | Plant Load Factor (PLF) |  | % | 0 | 0
C.3 | Normalised Loading Factor | As per 'NF-3 (14) - 'NF-3 APC'!E18 | % | 0 | 0
C.4 | Gross Operating Heat Rate | As per Form Sh (6. 1) - Form Sh'!K49 | kcal/kwh | 0 | 0
C.5 | Auxiliary Power Consumption (APC) | As per Form Sh (7. (vi)) - Form Sh'!F62 | MU | 0 | 0
C.6 | Auxiliary Power Consumption (APC%) | As per Form Sh (7. (vii)) - Form Sh'!F63 | % | 0 | 0
D | Heat Rate Configuration and Baseline Target Setting
D.1 | Station Design Net Heat Rate (DNHR) | B. 1 / (1- C. 6/100) | kcal/kwh |  | 0
D.2 | Station Operating Net Heat Rate (ONHR) | C.4 /(1- C.6 /100) | kcal/kwh |  | 0
D.3 | Difference in DNHR and ONHR | BY - (D.2 - D.1 ) | kcal/kwh |  | 0
D.4 | Deviation % from DNHR | D.3 *100/D.1 | % |  | 0
D.5 | Reduction Target for Deviation in Net Station Heat Rate (%) | AY = IF(BY(D.4) <=5, 10, IF(AND(BY(D.4) >5, BY(D.4)<=10), 17, IF(AND(BY(D.4) >10, BY(D.4)<=20), 21, IF(BY(D.4)>20, 24,0)))), BY = A.7 | % | 0 | 0
D.6 | Net Heat Rate reduction target | (D.5) x (D.3)/100 | kcal/kwh |  | 0
D.7 | Baseline Normalisation | (A.8)-(D.6) | kcal/kwh |  | 0
E | Normalisation in Operating Parameters
E.1 | Coal Quality
E.1.1 | Boiler Efficiency due to Coal Quality | As per NF-1 Coal Quality , S. No. 18 | % | 0
E.1.2 | Station Turbine Heat Rate to be Normalised due to Coal Quality | As per NF-1 Coal Quality , S. No. 16 | kcal/kwh | 0
E.2 | PLF & APC
E2.1 | NHR to be normalised for change in PLF in AY and corresponding effect on % APC | As per NF-2 PLF and APC Sr. No.44 | kcal/kwh | 0
E.3 | Gas Fuel Mix
E.3.1 | Notion energy for Fuel Mix to be Normalised for station | As per 'NF-4 Gas Fuel Mix' Sr No 12 | Million kcal | 0
E.3.2 | Heat Rate Normalisation for Gas Fuel mix | AY = E.5.1 / C.1 | kcal/kwh | 0
E.4 | Gas OC Cycle
E.4.1 | Notional energy for Gas OC Cycle to be Normalised for station | As per NF-5 Gas OC Cycle' Sr. No. 12 | Million kcal | 0
E.4.2 | Heat Rate Normalisation for Gas OC Cycle | AY = E.6.1 / C.1 | kcal/kwh | 0
E.5 | Gas Quality
E.5.1 | Notional energy for Gas Quality to be Normalised for station | NF-6 Gas NCV [7] | Million kcal | 0
E.5.2 | Heat Rate Normalisation for Gas Quality | E.7.1/C.4 | kcal/kwh | 0
E.6 | Others
E.6.1 | Total Energy to be normalised due to Start-ups/ Shutdowns/Environmental Concern/Unforeseen Circumstances | As per 'NF-7 Others' Sr. No. 10 | Million kcal | 0
E.6.2 | Heat Rate Normalisation for others | E.4.1 /(C.1-C.5) | kcal/kwh | 0
E.7 | Fuel mix for TPP
E.7.1 | Notional energy for Fuel Mix to be Normalised for station | As per 'NF-7 Others' Sr. No. 10 | Million kcal | 0
E.7.2 | Heat Rate Normalisation for others | E.4.1 /(C.1-C.5) | kcal/kwh | 0
F | Coal/Oil-Gas Based Thermal Power plant Normalised Operating Heat Rate Calculation
F.1 | Operating Heat Rate
F.1.1 | Station Operating Gross Heat Rate | IF('General Information' Sr. No. 3 ="Coal/Lignite/Oil/Gas Fired",C.4,"Not Applicable") | kcal/kwh | 0
F.2 | Coal Based Thermal Power Plant Station Operating Net Heat Rate without Normalisation | IF('General Information' Sr. No. 3 ="Coal/Lignite/Oil/Gas Fired",F.1.1/(1-C.6/100),"Not Applicable") | kcal/kwh | 0
F.3 | Normalisation
F.3.1 | Coal Quality Normalisation | E.1.2 | kcal/kwh | 0
F.3.2 | PLF and APC Normalisation | E2.1 | kcal/kwh | 0
F3.3. | Others Normalisation | E6.2 | kcal/kwh | 0
F.3.4 | Fuel mix for TPP (if applicable) | E7.2 | kcal/kwh | 0
F.4 | Coal Based Thermal Power plant Normalised Operating Net Heat Rate | IF('General Information' Sr. No. 3 ="Coal/Lignite/Oil/Gas Fired",F.1.2 -F.2.1 -F.2.2 - F.2.3 - F.2.4-D.7,"Not Applicable") | kcal/kwh | 0
G | Gas Based Thermal Power plant Normalised Operating Heat Rate Calculation
G.1 | Oprating Heat Rate
G.1.1 | Station Gross Operating Heat Rate | IF(OR('General Information' Sr. No. 3 ="Gas Turbine (Open Cycle)", 'General Information' Sr. No. 3 ="Combined Cycle Gas Turbine (CCGT)"),C.4 ,"Not Applicable") | kcal/kwh | Not Applicable
G.2 | Gas Based Thermal Power Plant Station Net Operating Heat Rate without Normalisation | IF(OR('General Information' Sr. No. 3 ="Gas Turbine (Open Cycle)",'General Information' Sr. No. 3 ="Combined Cycle Gas Turbine (CCGT)"),(G.1.1/(1- C.6/100)),"Not Applicable") | kcal/kwh | Not Applicable
G.3 | Normalisation
G.3.1 | PLF and APC Normalisation | E2.3 | kcal/kwh | Not Applicable
G.3.2 | Gas Fuel Mix Normalisation | E.5.2 | kcal/kwh | Not Applicable
G.3.3 | Gas OC Cycle Normalisation | E.6.2 | kcal/kwh | Not Applicable
G.3.4 | Gas Quality Normalisation | E7.2 | kcal/kwh | Not Applicable
G.3.5 | Others Normalisation | E.4.2 | kcal/kwh | Not Applicable
G.4 | Gas Based Thermal Power Plant Normalised Operating Net Heat Rate | IF(OR('General Information' Sr. No. 3 ="Gas Turbine (Open Cycle)",'General Information' Sr. No. 3 ="Combined Cycle Gas Turbine (CCGT)"),G.1.2 - G.2.1 - G.2.2 -G.2.3 - G.2.4-G.2.5-G.2.6-D.7,"Not Applicable") | kcal/kwh | Not Applicable
H | Diesel Generator Normalised Operating Heat Rate Calculation
H.1 | Operating Heat Rate
H.1.1 | Station Gross Operating Heat Rate | IF(D25="DG Set",E81,"Not Applicable") | kcal/kwh | Not Applicable
H.2 | Diesel Generator Operating Net Heat Rate without Normalisation | IF(D25="DG Set",E81/(1-E42/100),"Not Applicable") | kcal/kwh | Not Applicable
H.3 | Normalisation
H.3.1 | PLF and APC Normalisation | E2.3 | kcal/kwh | Not Applicable
H.3.2 | Others Normalisation | E4.2 | kcal/kwh | Not Applicable
H.4 | Diesel Generator Plant Normalised Operating Net Heat Rate | IF('General Information' Sr. No. 3 ="DG Set",H.1.2-H.2.1-H.2.2-D.7,"Not Applicable") | kcal/kwh | Not Applicable

## Form Sh
Form Sh (Details of Generation and Energy Consumption)
Sector - Thermal Power Plant
1 | Name of Thermal Power Plant |  |  | 0
2 | Year of Establishment |  |  | 0
3 | Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
4 | Plant Details
Sr No | Item |  |  | Current/ Assessment/ Target Year (2019-2020) | [7 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
i | Total Capacity (MW)
ii | Unit/Module Configuration (i.e. 3x100 + 2x250 + 2x500+ ------- etc.)
iii | Notified Baseline Net Heat Rate (kcal/kWh)
iv | Notified Target Net Heat Rate (kcal/kWh)
v | Notified Net Product output (Net Generation) in Million Units
vi | % Reduction Target for Percentage deviation in the Station Net Heat Rate as per Notificataion
5 | Unit /Module wise Design Data Details (For major fuel)
Sr No | Units@@ | Nomenclature of Units as per Standard Practice of TPPs | COD (dd/mm/yyyy) or (dd-mm-yyyy) | Design Capacity | As Provided by Original Equipment Manufacturer (OEM) |  |  | As established during Performance Guarantee Test (PG Test) ** |  |  | Curve Equation/ (R2) |  |  |  |  | Load Vs Heat Rate or HBD (at 100% Load) as per curve | Design Gas Turbine Heat Rate at 100% loading |  |  | Design Fuel Type (Coal/Lignite/ Gas/Naptha/ Oil/Other) | Source of Data
[5 empty] | Boiler Efficiency | Turbine Heat Rate (Coal based TPP) | Unit Heat Rate* | Boiler Efficiency | Turbine Heat Rate (Coal based TPP) | Unit Heat Rate | OEM Curve or HBD data curve |  | Constant 1 | Constant 2 | Constant 3 | Turbine Heat Rate | Module Heat Rate with Naphtha (For Gas based Power station) | Module Heat Rate with Oil/Other Fuel (For Gas based Power station) | Module Heat Rate Open Cycle (Major Fuel)
|  |  | Date | MW | % | kcal/kWh | kcal/kWh | % | kcal/kWh | kcal/kWh | y=ax2-bx+c | R2 | a | b | c | kcal/kWh | kcal/kWh | kcal/kWh | kcal/kWh
i | Unit1 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
ii | Unit2 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
iii. | Unit3 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
iv. | Unit4 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
v | Unit5 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
vi | Unit6 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
vii | Unit7 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
viii | Unit8 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
ix | Unit9 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
x | Unit10 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
xi | Unit11 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
xii | Unit12 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
xiii | Unit13 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
xiv | Unit14 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
xv | Unit15 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
5.1 | Station Design Data Details *** |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0
5.2 | Unit /Module wise Design Data Details (For other fuel)
i | Unit1 | [5 empty] | 0 |  |  | 0
ii | Unit2 | [5 empty] | 0 |  |  | 0
iii. | Unit3 | [5 empty] | 0 |  |  | 0
iv. | Unit4 | [5 empty] | 0 |  |  | 0
v | Unit5 | [5 empty] | 0 |  |  | 0
5.3 | Note
i | *** Weighted Average except for Design Capacity [For ex (Coal Fired): Station Design Heat Rate = {(DGHR 1 x Capacity 1 + DGHR 2 x Capacity2 + -----------) / (Total Capacity of Station)}] and [For ex (Gas Turbine):Station Operating Heat Rate={(Module HR 1 x Capacity 1 + Module HR 2 x Capacity2 + -----------) / (Total Capacity of Station Module)}
ii | ** To be indicated only if OEM certified design or PG Test report is available and the same can be produced as documentry proof, whenever required. If gas/liquid fuel is used, the Design/PG value for gas/liquied fuel may be given separately.
iii | * For Coal Based TPP- Unit Heat Rate (kcal/kWh) = [ Turbine Heat Rate (kcal/kWh) / Boiler Efficiency (%) ]
iv | @For Gas Turbine- Module Heat Rate (kcal/kWh) = [Design Fuel Input (NCV-kcal)/ Design Gross Out Put (kWh)]
v | @@ Module stands for Gas Power Station (referred as Combined setup of GT and ST)
vi | For other Fuel data, plant to insert the data in section 5.2 with Unit Nos
6 | Unit/Module wise Operating Data Details
Sr No | Units |  |  | Current/ Assessment/ Target Year (2019-2020) | [7 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
|  |  |  | Operating Load # |  | Loading Factor |  | Gross Generation |  | Unit Gross Heat Rate## |  | Operating Load |  | Loading Factor |  | Gross Generation |  | Unit Gross Heat Rate ##
|  |  |  | MW |  | % |  | MU |  | kcal/kWh |  | MW |  | % |  | MU |  | kcal/kWh
i | Unit1
ii | Unit2
iii. | Unit3
iv. | Unit4
v | Unit5
vi | Unit6
vii | Unit7
viii | Unit8
ix | Unit9
x | Unit10
xi | Unit11
xii | Unit12
xiii | Unit13
xiv | Unit14
xv | Unit15
6.1 | Station Operating Data Details ## |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
6.2 | Note
i | # Unit/Module Gross Generation in kWh in a year / Plant running hours in hrs in a year
ii | ## Heat rate = Total Fuel Consumed in the unit or module /Total Generation
iii | Weighted Average except for Operating Capacity [For ex (Coal Fired): Station Operating Heat Rate = {(OGHR 1 x Capacity 1 + OGHR 2 x Capacity2 + -----------) / (Total Capacity of Station)}] and [For ex (Gas Turbine):{(Station Operating Heat Rate=Module HR 1 x Capacity 1 + Module HR 2 x Capacity2 + -----------) / (Total Capacity of Station Module)}
7 | Station's Generation, PLF & Other Details
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (2019-2020) | [6 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
i | Station Installed Capacity |  |  | MW | 0 | [6 empty] | 0
ii | If COD of some unit(s) is in between the year, total station's weighted capacity for the year $ |  |  | MW
iii | Actual Gross Generation |  |  | MU | 0 | [6 empty] | 0
iv. | Plant Availability Factor |  |  | % | 1 | [6 empty] | 1
v | Annual PLF (Weighted)$$ |  |  | %
vi | Auxiliary Power Consumption $$$ (as per Sr. no 9(iv)) |  |  | MU | 0 | [6 empty] | 0
vii | Auxiliary Power Consumption $$$ (as per Sr No 7(iii) &7(vi)) |  |  | % | 0 | [6 empty] | 0
viii | Operating Gross Heat Rate |  |  | kcal/kWh | 0 | [6 empty] | 0
ix | Net Operating Heat Rate (kcal/kWh) $$$$ |  |  | kcal/kWh | 0 | [6 empty] | 0
x | Average PLF during Baseline year as per baseline energy audit reports |  |  | %
xi | Actual PLF as reported to CERC/SERC |  |  | %
xii | Operation Norms for Thermal Power Stations Gross Heat Rate Tariff Period - 2014 - 19 as per CERC/SERC |  |  | kcal/kWh
xiii | Station Net Operating Heat Rate as per Notification (Baseline) |  |  | kcal/kWh | [7 empty] | 0
xiv | Station Net Target Heat Rate as per Notification (Baseline) | [10 empty] | 0
7.1 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii) in case of Gas based Power Station or Thermal Oil-Gas based Plant)
Sr No | Item | Unit | Current/ Assessment/ Target Year (2019-2020) | [8 empty] | Baseline Year/ Previous Year (2015-2016)
|  |  | Actual Gross Generation-Closed Cycle |  |  | Actual Gross Generation-Open Cycle due to Internal factor |  |  | Actual Gross Generation-Open Cycle due to External factor |  |  | Actual Gross Generation-Closed Cycle |  |  | Actual Gross Generation-Open Cycle due to Internal factor |  |  | Actual Gross Generation-Open Cycle due to External factor |  |  | Source of Data
|  |  | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel | Gas | Naptha | Oil/Other Fuel
i | Unit1 | MU
ii | Unit2 | MU
iii. | Unit3 | MU
iv. | Unit4 | MU
v | Unit5 | MU
vi | Unit6 | MU
vii | Unit7 | MU
viii | Unit8 | MU
ix | Unit9 | MU
x | Unit10 | MU
xi | Unit11 | MU
xii | Unit12 | MU
xiii | Unit13 | MU
xiv | Unit14 | MU
xv | Unit15 | MU
| Total | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.2 | Station's Generation, PLF & Other Details (Bifurcation of Sr No 7(iii), 7(vi) in case of Gas based Power Station)
Sr No | Item | Units | Current/ Assessment/ Target Year (2019-2020) | [8 empty] | Baseline Year/ Previous Year (2015-2016) | [8 empty] | Source of Data
|  |  | Gas |  |  | Naptha |  |  | Oil/Other Fuel |  |  | Gas |  |  | Naptha |  |  | Oil/Other Fuel
i | Auxiliary Power Consumption | MU
ii | Actual Gross Generation-Closed Cycle | MU | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
iii | Actual Gross Generation -Open Cycle due to internal factor | MU | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
iv | Actual Gross Generation-Open Cycle due to external factor | MU | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
v | Actual Gross Generation |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
vi | Auxiliary Power Consumption | % | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
7.3 | Remarks
i | $ For example : if the COD of a 200 MW unit is 1st October in the current year, its weighted capacity for the whole year is 100 MW
ii | $$ Example-For Calculating ULF of the unit commissioned during the year : if the COD of a 200 MW unit is 1st October and PLF for the remaining period is 80% , its weighted capacity for the whole year is 100 MW, with weighted for whole year PLF stands at 40%
iii | $$$Power Consumption for Colony & Construction to be excluded
iv. | $$$$Net Heat Rate = [Gross Heat Rate / (1 - % APC)]
v | Note:In case of Gas based Power Station, the APC% for Gas/Liquid fuel may be given separately
8 | Details of Electricity Purchased from the Grid (MUs)
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (2019-2020) | [6 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
i | Purchased Electricity |  |  | MUs
ii | Reason
9 | Details of Electricity Generated and Auxiliary Power Consumption
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (2019-2020) | [6 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
i | Total Gross Generation of Electricity |  |  | MU | 0 | [6 empty] | 0
ii | Total Net Electricity Supplied to Grid |  |  | MU | 0 | [6 empty] | 0
iii | Electricity Consumption-Colony/Construction |  |  | MU
iv. | Total Electricity used inhouse for Power Generation i.e. APC (Without colony, construction & others consumption) |  |  | MU
v | Any other (specify) |  |  | MU
10 | Unitwise Fuel Analysis Details (As Fired Basis)@ (Not to be filled up for Gas based Power Station)
10. 1. | Coal/Lignite Fuel
A. | Unit-1
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
B | Unit-2
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
C | Unit-3
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
D | Unit-4
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
E | Unit-5
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
F | Unit-6
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
G | Unit-7
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
H | Unit-8
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
I | Unit-9
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
J | Unit-10
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
K | Unit-11
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
L | Unit-12
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
M | Unit-13
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
N | Unit-14
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
O | Unit-15
a | Proximate Analysis
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
[7 empty] | (Weighted Average)@@ |  |  |  |  | (Weighted Average)@@ | [5 empty] | Value
i. | Fixed Carbon |  |  | % | [13 empty] | 0
ii. | Volatile Matter |  |  | % | [13 empty] | 0
iii. | Total Moisture |  |  | % | [13 empty] | 0
iv. | Ash |  |  | % | [13 empty] | 0
v. | GCV |  |  | kcal/Kg | [13 empty] | 0
b | Ultimate Analysis
i | Carbon |  |  | % | [13 empty] | 0
ii. | Hydrogen |  |  | % | [13 empty] | 0
iii. | Nitrogen |  |  | % | [13 empty] | 0
iv. | Sulphur |  |  | % | [13 empty] | 0
v. | Oxygen |  |  | % | [13 empty] | 0
c | Fuel Blending Ratio | [16 empty] | 0
d | Electrical Energy Consumption for Coal Grinding Mills (VRM/Ball) + ID Fan + Ash Handling Plant |  |  | Million kWh | [13 empty] | 0
10.1.1 | Note
i | If Ultimate Analysis value is not available with DCs, Conversion from Proximate to Ultimate will be applied conversion formulae. %C = 0.97C+ 0.7(VM+0.1A) - M(0.6-0.01M) %H2= 0.036C + 0.086 (VM -0.1xA) - 0.0035M2(1-0.02M) %N2= 2.10 -0.020 VM Where: C= % of fixed carbon , A= % of ash ,VM= % of volatile matter, M= % of moisture
ii | In case of difference in Design Coal Quality for different units, Coal analysis to be given unitwise, otherwise enter the same parameter
10.1.2 | @ Attach all necessary Documents -
A | Coal Analysis:
i | Operating Coal Quality- Monthly average of the lots (As Fired Basis),Test Certificate for Coal Analysis including Proximate and Ultimate analysis (Minimum of 1 Samples per month for proximate analysis and 1 sample per quarter for utlimate analysis from NABL accredited external Lab-for cross verification)
ii | Performance Guarantee Test (PG Test) report from Original Equipment Manufacturer (OEM)
iii | Design Coal Analysis Document as per OEM
B | Boiler Efficiency
i | Design Boiler Efficiency Document from Original Equipment Manufacturer (OEM)
ii | @@ Weighted Average for the year: the sum of the tested coal of each lot as fired multiplied with the quantity of each lot , to be divided by the total fuel quantity during the year.
10.2 | Gas/Naptha/Furnace Oil Chemical and Physical Analysis used in Gas based Power Plant
Sr No | Element |  |  | Units | Design Fuel | PG Test Fuel | Current/ Assessment/ Target Year (2019-2020) |  |  |  |  | Baseline Year/ Previous Year (2015-2016) | [5 empty] | Value |  | Source of Data
10.2.1 | Gas Chemical and Physical Analysis
i | Methane (CH4) |  |  | % | [13 empty] | 0
iii | Ethane (C2H6) |  |  | % | [13 empty] | 0
iv | Propane (C3H8) |  |  | % | [13 empty] | 0
v | Other Hydro Carbons (C4+) |  |  | % | [13 empty] | 0
vi | Hydrogen |  |  | % | [13 empty] | 0
vii | Nitrogen |  |  | % | [13 empty] | 0
viii | Wobbe Index |  |  | No | [13 empty] | 0
ix | Methane No |  |  | No | [13 empty] | 0
x | Relative density (Specific Gravity) |  |  | kg/NM3 | [13 empty] | 0
xi | GCV |  |  | kcal/NM3 | [13 empty] | 0
xii | NCV |  |  | kcal/NM3 | [13 empty] | 0
10.2.2 | Naptha Analysis
i | GCV |  |  | kcal/kg | [13 empty] | 0
ii | NCV |  |  | kcal/kg | [13 empty] | 0
10.2.3 | Furnace Oil Analysis
i | GCV |  |  | kcal/kg | [13 empty] | 0
0
10.2.2 | Remarks:
i | Gas based Power station, The design heat rate given by either OEM or taken from HBD for the site rated ambient condition or PG test value will be taken for calculation
ii | Due to some unforeseen reasons, if Gas Turbine is operating in Open Cycle, separate documents should be maintained by the Plant for baseline as well as for assessment year
iii | Gas Supplier Fuel Analysis Documents should be available with Plant.
iv | For Mixed fuel such as Gas, Furnace Oil & Naphtha, documents related to design details of Gas/Furnace Oil/Naphtha maybe given separately.
11 | Details of Fuel Consumption (for calculation of heat rate, only as fired to be used)
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (2019-2020) | [6 empty] | Baseline Year/ Previous Year (2015-2016) | [5 empty] | Value |  | Source of Data
11.1 | Solid Fuel
a | Coal/Lignite (domestic)
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific Value (of coal at unloading end) |  |  | kcal/kg
iii | Moisture content (of coal at unloading end) |  |  | %
iv | Gross Calorific Value (of as fired coal sample) |  |  | kcal/kg © | [13 empty] | 0
v | Opening Stock as on 1st April (start of financial year) |  |  | Tonne
vi | Closing stock as on 31st March (closing of the financial year) |  |  | Tonne
vii | Total quantity received during the year |  |  | Tonne
viii | Total Coal/Lignite Consumption |  |  | Tonne | [13 empty] | 0
ix | Specific Coal/Lignite Consumption |  |  | Kg/kWh | [13 empty] | 0
b | Imported Coal | [16 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific Value (of coal at unloading end) |  |  | kcal/kg
iii | Moisture content (of coal at unloading end) |  |  | %
iv | Gross Calorific Value (of as fired coal sample) |  |  | kcal/kg © | [13 empty] | 0
v | Opening Stock (as on 1st April) (start of financial year) |  |  | Tonne
vi | Closing stock (as on 31st March) (closing of the financial year) |  |  | Tonne
vii | Total quantity received during the year |  |  | Tonne
viii | Total Coal/Lignite Consumption |  |  | Tonne | [13 empty] | 0
ix | Specific Coal/Lignite Consumption |  |  | Kg/kWh | [13 empty] | 0
c | Other Solid fuels | [16 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific Value (at unloading end) |  |  | kcal/kg
iii | Moisture content (at unloading end) |  |  | %
iv | Gross Calorific Value (of as fired sample) |  |  | kcal/kg © | [13 empty] | 0
v | Opening Stock (as on 1st April) (start of financial year) |  |  | Tonne
vi | Closing stock (as on 31st March) (closing of the financial year) |  |  | Tonne
vii | Total quantity received during the year |  |  | Tonne
viii | Total Consumption |  |  | Tonne | [13 empty] | 0
ix | Specific solid fuel Consumption |  |  | Kg/kWh | [13 empty] | 0
11.2 | Liquid Fuel ℗ | [16 empty] | 0
a | Liquid Fuel (LSHS/HSHS/LDO/Any Other) | [16 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific value |  |  | kcal/kg© | [13 empty] | 0
iii | Total Oil Consumption |  |  | KL | [13 empty] | 0
iv | Specific Oil Consumption for Coal/Gas fired Power Station |  |  | ml/kWh | [13 empty] | 0
v | Specific Oil Consumption for DG Set Station |  |  | Litre/kWh | [13 empty] | 0
b | Liquid Fuel (Naptha/ FO/Any Other) | [16 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific value |  |  | kcal/kg© | [13 empty] | 0
iii | Total Oil Consumption |  |  | KL | [13 empty] | 0
iv | Specific Oil Consumption for Coal/Gas fired Power Station |  |  | ml/kWh | [13 empty] | 0
v | Specific Oil Consumption for DG Set Station |  |  | Litre/kWh | [13 empty] | 0
c | Liquid Fuel (Any Other) | [16 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/Tonne | [13 empty] | 0
ii | Gross Calorific value |  |  | kcal/kg© | [13 empty] | 0
iii | Total Oil Consumption |  |  | KL | [13 empty] | 0
iv | Specific Oil Consumption for Coal/Gas fired Power Station |  |  | ml/kWh | [13 empty] | 0
v | Specific Oil Consumption for DG Set Station |  |  | Litre/kWh | [13 empty] | 0
11.3 | Gaseous Fuel | [16 empty] | 0
a | Type of Gas Fuel |  |  | NG | [13 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/SCM | [13 empty] | 0
ii | Gross Calorific value |  |  | (kcal/NM³)© | [13 empty] | 0
iii | Total Gas Consumption |  |  | Million NM³ | [13 empty] | 0
iv | Specific Gas Consumption |  |  | NM³/kWh | [13 empty] | 0
b | Type of Gas Fuel |  |  | RLNG/LNG/ Others | [13 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/SCM | [13 empty] | 0
ii | Gross Calorific value |  |  | (kcal/NM³)© | [13 empty] | 0
iii | Total Gas Consumption |  |  | Million NM³ | [13 empty] | 0
iv | Specific Gas Consumption |  |  | NM³/kWh | [13 empty] | 0
c | Type of Gas Fuel |  |  | APM | [13 empty] | 0
i | Landed Cost of fuel (Last purchase) [Basic Cost+Taxes+Freight] |  |  | Rs/SCM | [13 empty] | 0
ii | Gross Calorific value |  |  | (kcal/NM³)© | [13 empty] | 0
iii | Total Gas Consumption |  |  | Million NM³ | [13 empty] | 0
iv | Specific Gas Consumption |  |  | NM³/kWh | [13 empty] | 0
11.3.1 | Note
i | ℗Note: In case of Liquid fuels, take care of Density during calculations
ii | ©Weighted Average GCV i.e. sum of Heat value found in kcal in each lot on As Fired Basis, & analysed (tested) and fired during the year divided by total quantity of fuel fired during the financial year
12.1 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors
Sr No | Units |  |  | Current/ Assessment/ Target Year (2019-2020) | [7 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
|  |  |  | Loss of generation caused by low ULF/MLF due to Fuel Unavailability @, when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to Scheduling @, when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to backing down@,when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to any other external factor@,when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to Fuel Unavailability @,when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to Scheduling @,when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to backing down@,when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to any other external factor@,when the machine was on bar
|  |  |  | MU |  | MU |  | MU |  | MU |  | MU |  | MU |  | MU |  | MU
i | Unit1
ii | Unit2
iii. | Unit3
iv. | Unit4
v | Unit5
vi | Unit6
vii | Unit7
viii | Unit8
ix | Unit9
x | Unit10
xi | Unit11
xii | Unit12
xiii | Unit13
xiv | Unit14
xv | Unit15
| Total |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12.1.1 | @ External Factors:Non-Avaialability of fuel/schedule/backing down/any other external factor/Unforeseen factors
12.2 | Loss of PLF due to non-availability of fuel/schedule/backing down/any external factor/Unforeseen factors/Internal Factor
Sr No | Units |  | Capacity | Current/ Assessment/ Target Year (2019-2020) | [7 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
|  |  |  | Reserve Shutdown | Forced Outage/ Unavailability | Planned Maintenance Outage /Planned Unavailability | Unit Availability Factor | Loss of Generation caused by low ULF/MLF due to Internal factor ,when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to external factor, when the machine was on bar |  | Reserve Shutdown | Forced Outage/ Unavailability | Planned Maintenance Outage/ Planned Unavailability | Unit Availability Factor | Loss of Generation caused by low ULF/MLF due to Internal factor, when the machine was on bar |  | Loss of generation caused by low ULF/MLF due to external factor, when the machine was on bar
|  |  | MW | Hrs | Hrs | Hrs |  | MU |  | MU |  | Hrs | Hrs | Hrs |  | MU |  | MU
i | Unit1 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
ii | Unit2 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
iii | Unit3 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
iv | Unit4 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
v | Unit5 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
vi | Unit6 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
vii | Unit7 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
viii | Unit8 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
ix | Unit9 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
x | Unit10 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
xi | Unit11 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
xii | Unit12 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
xiii | Unit13 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
xiv | Unit14 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
xv | Unit15 |  | 0 |  |  |  | 1 |  |  | 0 |  |  |  |  | 1 |  |  | 0
| Total |  | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 0
@ External Factors:Non-Availability of fuel/schedule/backing down/any other external factor
12.2.1 | Documents Required
i | Characteristics Curve of Unit/Module Turbine Heat Rate Vs Load, from Original Equipment Manufacturer (OEM)
ii | Unit/Module wise HBD or Curve from Original Equipment Manufacturer (OEM) at various loads
iii | In case of non-availability of HBD or Curve, data from the similar Unit/Module will be considered
iv. | Design/PG Test Turbine/Module Heat Rate documents
12.3 | APC
Sr No | APC during Baseline year as per baseline energy audit reports | [18 empty] | Source of Data
%
i | 8.97
12.4 | Startup and Stoppages due external factor/Unforeseen factors
A | Nos of Startup and Shutdowns
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (2019-2020) | [6 empty] | Baseline Year/ Previous Year (2015-2016) | [5 empty] | Value |  | Remarks
[5 empty] | GTG (Gas) |  |  | STG (Coal/Gas/Diesel) |  |  |  | GTG (Gas) |  |  | STG (Coal/Gas/Diesel) |  |  | GTG (Gas) | STG (Coal/Gas/ Diesel)
i | Total Number of Shutdown in a year (Internal and External) |  |  | Nos | [13 empty] | 0 | 0
ii | Total Number of Shutdown in a year due to external factor |  |  | Nos | [13 empty] | 0 | 0
B | Energy Consumption during Shutdowns due to external factor
i | Total Electrical Energy consumption during shutdowns due to external factor |  |  | MU | [13 empty] | 0
12.4.1 | The DC may submit separate Excel sheet for additional information required for Heat Rate calculation or Normalisation for different module combination or load (Start/Stop)
C | Energy Consumption during Startups (Cold/Warm/Hot) due to external factor for Coal based Thermal Power Plant
Sr No | Units |  |  | MW | Current/ Assessment/ Target Year (2019-2020) |  |  | Baseline Year/ Previous Year (2015-2016) | [8 empty] | Value |  |  | Remarks
[5 empty] | Cold Start | Warm Start | Hot Start | Cold Start |  |  | Warm Start |  |  | Hot Start |  |  | Cold Start | Warm Start | Hot Start
[5 empty] | Nos | Nos | Nos | Nos |  |  | Nos |  |  | Nos |  |  | Nos | Nos | Nos
i | Unit1 |  |  | 0 | [12 empty] | 0 | 0 | 0
ii | Unit2 |  |  | 0 | [12 empty] | 0 | 0 | 0
iii. | Unit3 |  |  | 0 | [12 empty] | 0 | 0 | 0
iv. | Unit4 |  |  | 0 | [12 empty] | 0 | 0 | 0
v | Unit5 |  |  | 0 | [12 empty] | 0 | 0 | 0
vi | Unit6 |  |  | 0 | [12 empty] | 0 | 0 | 0
vii | Unit7 |  |  | 0 | [12 empty] | 0 | 0 | 0
viii | Unit8 |  |  | 0 | [12 empty] | 0 | 0 | 0
ix | Unit9 |  |  | 0 | [12 empty] | 0 | 0 | 0
x | Unit10 |  |  | 0 | [12 empty] | 0 | 0 | 0
xi | Unit11 |  |  | 0 | [12 empty] | 0 | 0 | 0
xii | Unit12 |  |  | 0 | [12 empty] | 0 | 0 | 0
xiii | Unit13 |  |  | 0 | [12 empty] | 0 | 0 | 0
xiv | Unit14 |  |  | 0 | [12 empty] | 0 | 0 | 0
xv | Unit15 |  |  | 0 | [12 empty] | 0 | 0 | 0
12.4.1 | Documents
i | APC consumption records during startups and Shutdowns
ii | Fuel consumption (Coal/Lignite/Liquid Fuel/NG) Records during Cold/Warm/Hot startups
12.5 | Increase in APC consumption due to Environmental compliance
Sr No | Name of the Major Equipment Installed |  |  | Current/ Assessment/ Target Year (2019-2020) | [7 empty] | Baseline Year/ Previous Year (2015-2016) | [7 empty] | Source of Data
|  |  |  | Capacity | Section |  |  | Date of Commissioning | Additional Electrical Energy Consumption | Additional Thermal Energy Consumption | Remarks | Capacity | Name |  |  | Date of Commissioning | Additional Electrical Energy Consumption | Additional Thermal Energy Consumption | Remarks
[8 empty] | Date | MU | Million kcal | [5 empty] | Date | MU | Million kcal
i
ii
iii
iv
v
vi
vii
viii
ix
x
| Total | [7 empty] | 0 | 0 | [6 empty] | 0 | 0
12.5.1 | Documents required related to Environmental compliance
i | The DCs have to maintain documents for additional installation of Environmental Equipment- Commissioning details, Energy meter reading etc
ii | Document of CPCB/SPCB
12.6 | Additional Energy due to Unforeseen circumstances (External Factor)
Sr No | Item |  |  | Units | Current/ Assessment/ Target Year (2019-2020) | [6 empty] | Baseline Year/ Previous Year (2015-2016) | [5 empty] | BY/previous Yr |  | Source of Data
i | Total Electrical Energy consumption due to unforeseen circumstances (external factor) |  |  | MU | [13 empty] | 0
ii | Total Thermal Energy consumption due to unforeseen circumstances (external factor) |  |  | Million kcal | [13 empty] | 0
13 | Documentation for Normalisation
Sr No | Item |  |  |  | Current/ Assessment/ Target Year (2019-2020) | [6 empty] | Baseline Year/ Previous Year (2015-2016) |  | Year 2 |  | Year 3/ Previous Year (20.... 20....) |  | BY/previous Yr |  | Source of Data
(i) | NF-1 Coal Quality -Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(ii) | NF-2 PLF and APC-Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(vi) | NF-3 Gas Fuel Mix Document Available for Normalisation |  |  | Yes/No | No | [6 empty] | No |  | Yes |  | Yes |  | No
(vii) | NF-4 Gas OC Cycle Document Available for Normalisation |  |  | Yes/No | No | [6 empty] | No |  | Yes |  | Yes |  | No
(viii) | NF-5 Gas Qualiy-Document Available for Normalisation |  |  | Yes/No | No | [6 empty] | No |  | Yes |  | Yes |  | No
(ix) | NF-6 Others Factors-Document Available for Normalisation |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
(iii) | NF-7 Fuel Mix for TPP- Document Available for Normalization |  |  | Yes/No | Yes | [6 empty] | Yes |  | Yes |  | Yes |  | Yes
14 | Investment made and Saving Achieved |  |  | Annual
a | Investment made for achieving target |  |  | Million Rs
b | Thermal Energy Saving achieved during the year
b.1 | Solid Fuel
b.1.1 | Coal |  |  | Million kcal | [13 empty] | 0
b.1.2 | Lignite |  |  | Million kcal | [13 empty] | 0
b.1.3 | Petcoke |  |  | Million kcal | [13 empty] | 0
b.1.4 | Biomass/Waste |  |  | Million kcal | [13 empty] | 0
b.2 | Liquid Fuel (HSD/LDO/FO/Others) |  |  | Million kcal | [13 empty] | 0
b.3 | Gaseous Fuel (LPG/Propone/NG/CNG/PNG/LNG/Others) |  |  | Million kcal | [13 empty] | 0
c | Electrical Saving achieved during the year |  |  | Lakh kWh | [13 empty] | 0
15 | Process Flow Diagram Attached |  |  | Yes/No
16 | Machine Details
16.1 | Unit No. | Capacity (MW) | Boiler Manufacturer name (OEM) | Turbine manufacturer name (OEM) | Module manufacturer name (OEM) for Gas plants | PG Test Carried by (name of the vendor) | Last annual overhauling (AOH) date | last Capital overhauling (COH) date | Last R&M/ LE date
i | Unit1 | 0
ii | Unit2 | 0
iii | Unit3 | 0
iv | Unit4 | 0
v | Unit5 | 0
vi | Unit6 | 0
vii | Unit7 | 0
viii | Unit8 | 0
ix | Unit9 | 0
x | Unit10 | 0
xi | Unit11 | 0
xii | Unit12 | 0
xiii | Unit13 | 0
xiv | Unit14 | 0
xv | Unit15 | 0
Please enter numeric values or leave blank
0 | Please eneter numeric value or "0"
Fomulae Protected
Data not to be filled
Yes | Select from the list Yes or No
We ……………………………………………….........................…..........................undertake that information furnished in the Sector Specific Form I are complete and accurate to the best of my knowledge. I also undertake that the information provided for Normalisation is limited to external factors only.
| (Signature of the Energy Manager) | [12 empty] | (Signature of the Chief Executive)
| Name & designation of the Energy Manager: | [12 empty] | Name & designation of the Chief Executive:
EM/EA No:
Mobile No:
Organisation Seal:
Date:
Place:

## NF-1 Coal Quality
Normalization Factor for Fuel Quality in TPP
Name of the Thermal Power Station |  |  |  | 0
Documents Avaialbility |  |  |  | Yes | Yes | PAT-III
Sr No | Item | Basis/Calculation | Unit | Unit 1 |  |  | Unit 2 |  |  | Unit 3 |  |  | Unit 4 |  |  | Unit 5 |  |  | Unit 6 |  |  | Unit 7 |  |  | Unit 8 |  |  | Unit 9 |  |  | Unit 10 |  |  | Unit 11 |  |  | Unit 12 |  |  | Unit 13 |  |  | Unit 14 |  |  | Unit 15
|  |  |  | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY | Current Year [AY] | Baseline Year [BY] | Design [D] for AY
1 | Unit Capacity | As per Form Sh Sr. No. 4(i) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Turbine Heat Rate | IF('Form Sh' OEM THR [5.(i)]=0,'Form Sh' PG Test THR,'Form Sh' OEM THR [5.(i)]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Generation | As per Form Sh Sr. No. AY.[6.(i)] | MU | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
4 | Total Moisture | As per Form Sh Sr. No. 10.1.A.a.(iii) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Ash | As per Form Sh Sr. No. 10.1.A.a. (iv) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | GCV | As per Form Sh Sr. No. 10.1.A.a.(v) | kcal/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Hydrogen | As per Form Sh Sr. No. 10.1.A.b.(ii) | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | % Boiler Efficiency (As per Formulae) | 92.5- {50*[3] +630*([2]+9*[5])}/[4] | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Actual Design Boiler Efficiency of Unit (As per OEM) | As per Form Sh | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | % Decrease in Efficiency from calculated Boiler operating Efficiency to calculated Boiler Design Efficiency | AY=(D[8]-AY[8])/D[8], BY=(D[8]-BY[8])/D[8] | % | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
11 | Degradation/Upgradation of Actual Boiler Design Efficiency | AY=D[9]*AY[10]/100, BY=D[9]*AY[10]/100 | % | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
12 | Normalised Design Boiler Efficiency for Unit | IFERROR(D[9])- AY[11], 0), | % | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
13 | Difference in Normalised Boiler Efficiency between BY and AY | [12] (BY) - [12](AY) | % | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
14 | Normalised Gross Heat Rate for AY | [D](2)*100/AY(12) | kcal/kWh | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
15 | Heat Rate to be normalised in the Unit operating Heat Rate | IF(AY[13]<0,0,[14]-D[2] x100/BY[18]) | kcal/kWh | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
16 | Heat Rate to be normalised in the station operating Heat Rate | (U#1(AY[15]*AY[3])+ U#2 ((AY[15]*AY[3])+ U#3 ((AY[15]*AY[3]) +U#4 ((AY[15]*AY[3]) + U#5 ((AY[15]*AY[3]) + U#6 ((AY[15]*AY[3]) + U#7 ((AY[15]*AY[3]) + U#8 ((AY[15]*AY[3]) + U#9 ((AY[15]*AY[3]) + U#10 ((AY[15]*AY[3]))/(U#1 (AY[3]) + U#2 (AY[3]) + U#3 (AY[3]) + U#4 (AY[3]) + U#5 (AY[3]) + U#6 (AY[3]) + U#7 (AY[3]) + U#8 (AY[3]) +U#9 (AY[3]) + U#10 (AY[3])) | kcal/kWh | 0
17 | Normalised Boiler Efficiency Design for Unit for the AY as compared to the BY | IFERROR(IF(AY[13]<=0,BY[9],D[9] - AY[13]),0) | % | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
18 | Normalised Boiler Efficiency Design for Station | (U#1 (AY[17]*D[1]) + U#2 (AY[17]*D[1]) +U#3 (AY[17]*D[1]) +U#4 (AY[17]*D[1]) +U#5 (AY[17]*D[1]) + U#6 (AY[17]*D[1]) + U#7 (AY[17]*D[1]) + U#8 (AY[17]*D[1]) +U#9 (AY[17]*D[1]) + U#10 (AY[17]*D[1]))/(U#1 (D[1]) + U#2 (D[1]) +U#3 (D[1]) +U#4 (D[1]) +U#5 (D[1]) + U#6 (D[1]) +U#7 (D[1]) +U#8 (D[1]) +U#9 (D[1]) +U#10 (D[1])) | % | 0
19 | Unit Design Gross Heat Rate |  | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Station Design Gross Heat Rate |  | kcal/kWh | 0 | 0 | 0
21 | Station Design Boiler Efficiency |  | % | 0 | 0 | 0

## NF-2 PLF and APC
Normalization Factor for plant loading
Name of the Thermal Power Station |  |  |  | 0
Documents Avaialbility |  |  |  | Yes | Yes | PAT-III
S.No. | Unit nos. | Capacity (MW) | Generation (MU) |  | Constants |  |  |  | unit | Loading factors (%)
|  |  | AY | BY | a | b | c |  |  | 100 | 95 | 90 | 85 | 80 | 75 | 70 | 65 | 60 | 55 | 50 | 45 | 40 | 35 | 30
1 | U#1 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | U#2 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | U#3 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | U#4 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | U#5 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | U#6 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | U#7 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | U#8 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | U#9 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | U#10 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | U#11 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | U#12 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | U#13 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | U#14 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | U#15 | 0 | 0 | 0 | 0 | 0 | 0 | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Station | 0 | [5 empty] | Load | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | THR/ module HR | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Station
| Load | THR/ Module HR | APC (BY) | APC adjustment |  | loading factor (%) |  | Wt. Avg. boiler eff. | GHR | APC (calc.) | NHR
| MW | kcal/kWh | % | (%) per loading factor |  | BY | AY | % | kcal/kWh | % | kcal/kWh
| 0 | 0 | 0 | 0.025 |  | 0 | 0 | 0 | 0 | -2.5 | 0
| 0 | 0 | [6 empty] | 0 | -2.375 | 0
| 0 | 0 | [6 empty] | 0 | -2.25 | 0
| 0 | 0 | [6 empty] | 0 | -2.125 | 0
| 0 | 0 | [6 empty] | 0 | -2 | 0
| 0 | 0 | [6 empty] | 0 | -1.875 | 0
| 0 | 0 | [6 empty] | 0 | -1.75 | 0
| 0 | 0 | [6 empty] | 0 | -1.625 | 0
| 0 | 0 | [6 empty] | 0 | -1.5 | 0
| 0 | 0 | [6 empty] | 0 | -1.375 | 0
| 0 | 0 | [6 empty] | 0 | -1.25 | 0
| 0 | 0 | [6 empty] | 0 | -1.125 | 0
| 0 | 0 | [6 empty] | 0 | -1 | 0
| 0 | 0 | [6 empty] | 0 | -0.875 | 0
| 0 | 0 | [6 empty] | 0 | -0.75 | 0
18 | equation | y=aX^2-bX+c
| a | 0
| b | 0
| c | 0
19 | Weighted Average HR at 100% loading as per OEM | [5 empty] | kcal/kWh | 0
20 | Weighted Average HR at 100% loading as per Curve | [5 empty] | kcal/kWh | 0
21 | Deviation percentage between OEM and Curve design | [5 empty] | % | 0
22 | Station design NHR at 100% loading | [5 empty] | kcal/kWh | 0
26 | NHR reduction target w.r.t. 100% loading | [5 empty] | kcal/kWh | 0
27 | Target NHR notified | [5 empty] | kcal/kWh | 0
23 | Design NHR at BY loading (as per curve) | [5 empty] | kcal/kWh | 0
24 | Corrected Design NHR at BY loading (as per curve) | [5 empty] | kcal/kWh | 0
25 | Operating NHR in BY | [5 empty] | kcal/kWh | 0
28 | Difference between desing and operating at BY loading factor | [5 empty] | kcal/kWh | 0
29 | Deviation w.r.t. to design at BY loading | [5 empty] | % | 0
30 | Deviation slab applicable | [5 empty] | % | 0
31 | NHR reduction Target | [5 empty] | kcal/kWh | 0
32 | Maximum allowable deviation at BY loading | [5 empty] | kcal/kWh | 0
33 | Maximum allowable deviation at BY loading | [5 empty] | % | 0
35 | Target at any loading factor- Maximum allowable deviation from design at the corresponding loading factor | [5 empty] | % | 0
37 | Operating NHR in AY | [5 empty] | kcal/kWh | 0
38 | Design NHR at AY loading (as per curve) | [5 empty] | kcal/kWh | 0
39 | Corrected Design NHR at AY loading (as per curve) | [5 empty] | kcal/kWh | 0
40 | Target NHR at AY loading as per maximum allowable deviation | [5 empty] | kcal/kWh | 0
43 | Target normalization w.r.t. change in AY loading | [5 empty] | kcal/kWh | 0

## NF-3 Gas Fuel Mix
Normalization Factor for Fuel Mix in Gas based Power Station
Name of the Thermal Power Station |  |  |  | 0
Documentation Availability |  |  |  | No | No
Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Module-1 |  | Module-2 |  | Module-3 |  | Module-4 |  | Module-5 |  | Module-6 |  | Module-7 |  | Module-8 |  | Module-9 |  | Module-10 |  | Module-11 |  | Module-12 |  | Module-13 |  | Module-14 |  | Module-15
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | Remarks
1 | Unit Capacity | As per 'Form Sh' 5 (i) to 5 (x) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Module Heat Rate @ 100% Load (OEM) for Gas | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Design Module Heat Rate @ 100% Load for Naphtha | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Design Module Heat Rate @ 100% Load (OEM) for Oil/Other Fuel | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Actual Gross Generation from Gas | Form Sh' 7.1.(i) [OC-Gas]+ 'Form Sh' 7.1.(i)[CYI-Gas]+'Form Sh' 7.(i)[OCE-Gas] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Actual Gross Generation from Naphtha | Form Sh' 7.1.(i) [OC-Naphtha]+ 'Form Sh' 7.1.(i)[CYI-Naphtha]+'Form Sh' 7.(i)[OCE-Naphtha] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Actual Gross Generation from Oil/Other Fuel | Form Sh' 7.1.(i) [OC-Oil/Other Fuel]+ 'Form Sh' 7.1.(i)[CYI-Oil/Other Fuel]+'Form Sh' 7.(i)[OCE-Oil/Other Fuel] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Gross Generation from Fuel Mix | [5] + [6] + [7] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Module Heat Rate with Fuel Mix | ([2]*[5]+[3]*[6]+[4]*[7])/([5] + [6] + [7]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Difference in Assessment year w.r.t. Baseline Year | AY[9] - BY[9] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
11 | Notional energy for Fuel Mix to be Normalised for Module | [10]*[8] | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12 | Notional energy for Fuel Mix to be Normalised for station | M1[12] + M2[12] +….. | Million kcal | 0

## NF-4 Gas OC Cycle
Normalization Factor for Open and Closed cycle operation in Gas based Power Station
Name of the Thermal Power Station |  |  |  | 0
Documentation Availability |  |  |  | No | No
Type of Thermal Power Plant |  |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | Module-1 |  | Module-2 |  | Module-3 |  | Module-4 |  | Module-5 |  | Module-6 |  | Module-7 |  | Module-8 |  | Module-9 |  | Module-10 |  | Module-11 |  | Module-12 |  | Module-13 |  | Module-14 |  | Module-15
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY | Remarks
1 | Unit Capacity | As per 'Form Sh' 5. (i) to 5. (x) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Module Heat Rate @ 100% Load (OEM) for Closed Cycle | IF('Form Sh' OEM UHR [5.(I)] =0,'Form Sh' PG Test UHR [5.(I)],'Form Sh' OEM UHR [5.(I)]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Design Module Heat Rate @ 100% Load for Open Cycle | Form Sh' 5.(i) DHR at Different Condition [OC-MHR] | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Design Module Heat Rate @ 100% Load (OEM) for Oil/Other Fuel | Form Sh' 5.(i) DHR at Different Condition [Oil/Other Fuel - MHR] | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Actual Gross Generation during Closed Cycle | SUM('Form Sh' 7.1 (i) [CC-(Gas+ Naphtha + Oil/Others)] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Actual Gross Generation during Open Cycle due to external factor | SUM('Form Sh' 7.1 (i) [OCE-(Gas+ Naphtha + Oil/Others)] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Actual Gross Generation during Open Cycle due to internal factor | SUM('Form Sh' 7.1 (i) [OCI-(Gas+ Naphtha + Oil/Others)] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Gross Generation during Open Cycle (External Factor) and Closed Cycle operation | [10] + [11] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Module Heat Rate for Open and Closed Cycle Operation | ([2]*[5]+ [3]*[6]/([5] + [6]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Difference in Assessment year w.r.t. Baseline Year | AY[9] -BY[9] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
11 | Notion energy for Gas OC Cycle to be Normalised for Module | [10] * [8] | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
12 | Notion energy for Gas OC Cycle to be Normalised for station | M1[11] + M2 [11] + ………… | Million kcal | 0

## NF-5 Gas Quality
Normalization Factor for Gas Quality in Gas based Power Station
Name of the Thermal Power Station |  | 0
Documentation Availability |  |  |  | No | No
Type of Thermal Power Plant |  | Coal/Lignite/Oil/Gas Fired
Sr No | Item | Calculation/Basis | Unit | AY | BY
1 | Station Net Heat Rate (NHR) | Form Sh'! 7 (ix) AY & BY | kcal/kWh | 0 | 0
2 | Net Calorific Value of Gas | Form Sh'! 10.2.1 (xii) AY & BY | kcal/kg | 0 | 0
3 | NHR trendline equation | y = -10^-7x^2 + 0.0051x + 1490.5 | kcal/kWh | y = -10^-7x^2 + 0.0051x + 1490.5 | y = -10^-7x^2 + 0.0051x + 1490.5
4 | NHR as per trendline equation | y = -10^-7x^2 + 0.0051x + 1490.5 Where x=NCV | kcal/kWh | 1490.5 | 1490.5
5 | Difference in NHR as per trendlne Equation between AY and BY | (4)AY-(4)BY | kcal/kWh | 0
6 | Gross Generation in AY | Form Sh'! 6.1 Gr. Gen AY | Million Units | 0
7 | Normalization due to change in Gas Quality | (6)*(5) | Million Kcal | 0

## NF-6 Others
Normalization -Others (Startup/Shutdown/Environmental Concern)
Name of the Thermal Power Station |  | 0
Sr No | Unit | Calculation/Basis | MW | Baseline Year (BY) |  |  | Assessment Year (AY) |  |  | Difference (AY)-(BY) |  |  | kL Oil consumption |  |  | Remarks
|  |  |  | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start | Cold Start | Warm Start | Hot Start
1 | Unit 1 | Form Sh'! 12.4 c(i) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Unit 2 | Form Sh'! 12.4 c(ii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Unit 3 | Form Sh'! 12.4 c(iii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Unit 4 | Form Sh'! 12.4 c(iv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Unit 5 | Form Sh'! 12.4 c(v) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Unit 6 | Form Sh'! 12.4 c(vi) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Unit 7 | Form Sh'! 12.4 c(vii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Unit 8 | Form Sh'! 12.4 c(viii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Unit 9 | Form Sh'! 12.4 c(ix) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Unit 10 | Form Sh'! 12.4 c(x) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Unit 11 | Form Sh'! 12.4 c(xi) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Unit 12 | Form Sh'! 12.4 c(xii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Unit 13 | Form Sh'! 12.4 c(xiii) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Unit 14 | Form Sh'! 12.4 c(xiv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Unit 15 | Form Sh'! 12.4 c(xv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0
Documentation Availability |  |  |  | Yes | Yes
Sr No | Item | Calculation/Basis | Unit | Additional energy consumption in Assessment Year (AY) |  | Remarks
12 | Thermal Energy to be subtracted due to Cold/Warm/Hot Start up (External Factor) | (11CS+11WS+11HS)*10 | Million kcal | 0
13 | Electrical Energy to be subtracted due to Shutdown (External Factor) | Form Sh'! 12.4 B(i) | MU | 0
14 | Electrical Energy to be subtracted due to Environmental concern (External Factor) | Form Sh'! 12.5 Total Ad.El.En.Con. | MU | 0
15 | Thermal Energy to be subtracted due to Environmental concern (External Factor) | Form Sh'12.5 Total Ad.Th.En.Con. | Million kcal | 0
16 | Electrical Energy to be subtracted due to Unforeseen Circumstances (External Factor) | Form Sh'! 12.6 (i) | MU | 0
17 | Thermal Energy to be subtracted due to Unforeseen Circumstances (External Factor) | Form Sh'! 12.6 (ii) | Million kcal | 0
18 | Gross Heat Rate of Station | Form Sh'! 6.1 UGHR | kcal/kWh | 0
19 | Total Electrical Energy | AY={(13AY)+914AY)+(16AY)}*(18AY) BY={(13BY)+(16BY)}*(18BY) | Million kcal | 0
20 | Total Thermal Energy | AY=(15AY)+(17AY)+(12AY) BY=(17BY) | Million kcal | 0
21 | Total Energy to be subtracted | {(19AY)+(20AY)}-{(19BY)+(20BY)} | Million kcal | 0

## NF-7 Fuel Mix for TPP
Normalization Factor for Fuel Mix inThermal Power Station
Name of the Thermal Power Station |  | 0
Type of Thermal Power Plant |  | Coal/Lignite/Oil/Gas Fired
Documentation Availability |  |  |  | Yes | Yes
Sr No | Item | Calculation/Basis | Unit | Unit-1 |  | Unit-2 |  | Unit-3 |  | Unit-4 |  | Unit-5 |  | Remarks
|  |  |  | AY | BY | AY | BY | AY | BY | AY | BY | AY | BY
1 | Unit Capacity | As per 'Form Sh' 5 (i) to 5 (x) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Design Gross Heat Rate @ 100% Load (OEM) from Fuel 1 (Gas) | As per 'Form Sh' 5 (i) to 5 (x) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Design Gross Heat Rate @ 100% Load from fuel 2 (Oil/others) | As per 'Form Sh' 5.2 (i) to 5.2 (v) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Actual Gross Generation from Fuel 1 (Gas) | Form Sh' 7.1.(i) [OC-Gas]+ 'Form Sh' 7.1.(i)[CYI-Gas]+'Form Sh' 7.(i)[OCE-Gas] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Actual Gross Generation from Fuel 2 (Oil/ Others) | Form Sh' 7.1.(i) [Oil/others]+ 'Form Sh' 7.1.(i)[CYIOil/others]+'Form Sh' 7.(i)[Oil/others] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
s
6 | Gross Generation from Fuel Mix | [4] + [5] | MU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Gross Heat Rate with Fuel Mix | ([2]*[4]+[3]*[5])/([4] + [5]) | kcal/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Difference in Assessment year w.r.t. Baseline Year | AY[7] - BY[7] | kcal/kWh | 0 |  | 0 |  | 0 |  | 0 |  | 0
9 | Notional energy for Fuel Mix to be Normalised for Module | [9]*[6] | Million kcal | 0 |  | 0 |  | 0 |  | 0 |  | 0
10 | Notional energy for Fuel Mix to be Normalised for station | M1[9] + M2[9] +….. | Million kcal | 0

## Annex-loading factor
Annex_Loading Factor
Name of the Thermal Power Station |  | 0
Sr No | Item | Unit | Assessment Year (AY) | Baseline Year (BY) | Remarks
1 | Station Capacity | MW | 0 | 0
2 | Plant Availability Factor |  | 1 | 1
3 | Station total gross generation | MU | 0 | 0
4 | Station loss in generation due to external factors | MU | 0 | 0
5 | Station loss in generation due to internal factors | MU | 0 | 0
6 | Maximum generation possible as per availability factor | MU | 0 | 0
7 | Station Actual Loading Factor |  | 0 | 0
8 | Normalised Loading Factor |  | 0 | 0
9 | Cross Check |  | 0 | 0

## Annex example of load Vs THR
Turbine Heat Rate Vs Load
% Load | Gross Load (MW) | Heat Rate | Heat Rate as per Equation
% | MW | (kcal/kWh) | (kcal/kwh)
30.2857 | 63.6 | 2327.75 | 2333.2697
35.7143 | 75 | 2292.6 | 2284.92
47.619 | 100 | 2196 | 2194.36
59.5238 | 125 | 2116.65 | 2125.05
71.4286 | 150 | 2074.05 | 2076.99
83.3333 | 175 | 2057.4 | 2050.18
86.1905 | 181 | 2052 | 2046.9076
95.2381 | 200 | 2042.6 | 2044.62
100 | 210 | 2044.44 | 2048.346
12600